        CO2-W-TH-POE

CO2 Sensor with Temperature & Humidity
        & BACnet & Power Over Ethernet

GOTCHAS
11 April 2023

Power and Physical Connections

1. Requires IEEE 802.3af/at compliant POE Injector (54 Volts)
  1. specification sheet says 24 volts, but will not work with Passive POE standard (24 volts).
2. Ethernet Cable CAT6 (or better) with 1/2” bend radius to exit device
3. Should also be able to power with standard 24 Volt supply instead of POE

Boot-up

15 second boot-up: 11 second flashing white screen followed solid white screen

Ethernet

1. Design does not respond to Network Command “ipconfig”
2. Should respond to “ping ip address”